### Alternator Supplied Rectifier Exciter

This type of exciter is implemented in the MODES (see WWW.MODESINFO.COM) as model AC1A and correspond the same named model according IEEE. There are two differences:

- Alternator is modelled by function KA/(1+pTA) instead of 1/pTE with back loop KE  - transformation is kA =1/kE a  TA =T E /kE

- Exciter and regulator are modelled separately.

Fig. 1 Block  scheme of  Alternator Noncontrolled Rectifier AC1A

Transfer function FEX models noncontrolled rectifier:

1-0.577x                                     x<0.433

FEX=(0.75-x2)                      pro 0.433<x<0.75        x=kC*IB/UE	 (5.14)

1.732(1-x)                        0.75 <x<1.0

Saturation function is modelled as follows:

sE =ASS/UE*eBSUE  - e*BS*ASS                         for UE>1/BS	 (5.15)

sE =0                                                                 for UE<1/BS

Calculation of parameters is described in the following Example:

Example  Chyba! V dokumentu není žádný text v zadaném stylu.-1

Calculate parameters of  AC1A for generator 200 MW.

Parameters of main generator 200 MW: UGn=15.75 kV, no load filed voltage and current   UBO=120 V, IB0=900 A

Parameters of noncontrolled rectifier: UBmax= 994 V, UBmin=28 V

Parameters of auxiliary generator:  UEn=290 V, IEn=2000 A, Xd=1.41, Xd" =0.15, Td)’ =4 s,

no load filed voltage and current   Uf0=15 V, If0= 55A, saturation curve (open circuit characteristic) table:

| If [A] | 0 | 20 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 180 | 200 | 220 | 240 | 260 | 280 | 300 | 320 | 340 | 360 | 380 | 400 | 420 | 440 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| UE0 [V] | 0 | 107 | 208 | 324 | 409 | 494 | 571 | 637 | 687 | 710 | 741 | 765 | 787 | 803 | 819 | 842 | 857 | 872 | 880 | 896 | 911 | 927 | 934 |

Parameters of electronic amplifier (tyristor bridge): amplification KK=13, output limit UKmax= 130 V.

Parameters of controller: output limit URmax=500 V, proportional gain kP=10, measuring element gain KM=0.000667V~/V=.

Solution:

Because of the per unit system is used in the model, it is necessary to choose base values for excitation system components. For regulator we choose base value URv= KMUGn= 10.5 V, so that the per unit gain of the voltage measuring element is 1. For rectifier we choose no load filed voltage and current of the main generator UBO and   IBO. For aux. generator we choose base values no load nominal voltage and current of the auxiliary generator UEn and IEn.  The variables (bold) and base values are depicted on the top of following figure:

Fig. 2 Náhradní schéma pro výpočet parametrů střídavého budiče

For rectifier transfer in the first regime (when only one diode is commutating in the each branch of the bridge) is for named values:

UB =3/*(2UI –XCIB)  = 3/*2UI [1-Xd“*IB/ (2UI)]	(5.16)

UI is  a rms value of  auxiliary generator internal ems (corresponds the E“ ems), XC is commutation reactance - subtransient reactance of the auxiliary generator.

Auxiliary generator is possible (with simplification) to model by equation:

Td0'*Eq'° = Uf + (Xd-Xd')*Id- Eq'	(5.17)

where the variable Eq’ is replaced by Eq“ and transient   reactance Xd' by subtransient one Xd”.  Internal ems E“ is calculated from Eq“ dividing to cos where is internal angle between q axis   and phasor of E“.  Demagnetising effect of the direct component of load current is proportional of (Xd- Xd”). Direct component of load current corresponds multiplication of load current IG and sin because with neglected commutation voltage droop and in steady is load current and terminal voltage in phase (cos=1). Angle is for steady state constant independent on load condition and it is calculated from rectangle triangle (UB=IB for our per unit system.)-see Fig. Interface between the auxiliary generator and rectifier is created by two dashed blocks created by voltage and current ratios pU and pI, which transform generator pu terminal voltage into rectifier no load output voltage and vice verse field current into generator pu load current.

Since these current ratios are not in the IEEE models, they are included into generator gain kA and current gain kD.  Comparing of  Fig. 2 and Fig. 1 we obtain: KA=pU/cos, KC=3/Xd“(UEn/UBO)(IBO/IEn), KD=pI(Xd-Xd“)sin=argtag{(Xd-Xd“)pUpI}.

Then we can calculate = 55o , pU=3.26,  pI =0.35, KA =5.68, KC=0.156, KD=0.36. Time constant is  TA = Td)’ =4 s. We can use least squared method for estimation of saturation parameters for (5.15) from saturation curve. The solver  from the EXCEL application gives BS0= 2.09 a ASS0= 0.00593.

Fig. 3 Comparing of no load saturation curve (measured and approximation) and resulting rectifier curve

Since the back loop is from UE voltage in the model AC1A (no load rectifier voltage - without commutation voltage droop) it is necessary parameters ASS0 multiply a BS0 divide by voltage ratio pU, so that ASS= 0.0193 a BS= 0.641.