Modelling of Transient Phenomena

in the Power System

Program Application Guide

This guide describes the facilities available

in version 2.2. of the MODES network simulator

see www.modesinfo.com for more information about the MODES package

 Karel  Máslo  1994

Document Conventions

This guide uses the following typographic conventions for the descriptions of symbols, variables and parameters:

Y ... Bold capital letters indicate matrix and program key words

X ... Underlined letters are used for the complex variables

k ... Italics letters are used for per unit values

D ... Increment description

° ... Derivation description

Ö ... Square root description

[ ]... Equation reference

//... Literature reference

Real,Imag{X}.. Real and imaginary part of the complex number X

Abs,Arg{X}.... Magnitude and argument of the complex number X

'SYMB'........ Symbolic name of the equipment model

'ACTI'.......... Symbolic name of the action (method)

The meaning of some indexes:

" ' ................Description of the subtransient and transient values

dq ..............Indexes for the dq parts of Parks transformation

G, E, T .......Indexes of the generator,  exciter and turbine variab.

T,LOAD......Indexes of the transformers and load variables

n 0 k ...........Indexes of the nominal, no-load and short-circuit value

This rules is used for the block schemes drawing:

# Introduction

This guide serves as a basic introduction into the methods of the power system transient phenomena modelling, which are used in the program MODES.

It is assumed that the reader is familiar with the fundamental of electric network analysis (the symmetrical component theory and matrix calculations), elementary differential equation theory and the use of Laplace transfer function. The reader will also need to be known with the basic theory of principal power system equipment (generators, turbines, exciters and so on).

The object oriented approach is used. It is based on a description of each equipment as an object. These objects are described by models, theirs state and algebraic variables. The object models are linked by the coupling variables. Models introduce an abstract mathematical description of physical reality. This description has either the algebraic/differential form, or the operational form.

The models level depends on the purpose, which they are used for. The most detailed models are used by the equipment producers for the equipment design. The second level is created by the technology units models. These models must take into account the whole range of operational states. The network simulators introduce the third level. These models enable to simulate the network failures for example short-circuits, line or unit tripping and load changing.

The time range for the different types of transient phenomena and the equipment, affectng them, are in the figure below.

Fig.  1 Time ranges of transient phenomena in power system

The program MODES makes possible to simulate:

1.	transient stability of generators (loss of synchronism)

2.	middle-term dynamics concerned with the primary control of  frequency (frequency collapse)

3.	long term stability concerned with the LFC and with OLTC and the overcurrent limiter  actions (voltage  collapse).

4.	transient phenomena in home consumption of the units (driven start-up, switching over to back-up)

5.	steady state stability - investigation of the power system for a small deviation  (oscillations)

# Power system modelling

The power system consists of the number objects. It is useful to divide this system into generation, transmission and consumption parts, from the description point of view.  The power stations, the network and load correspond to that dividing. The power station consists of the individual units, the network consists of the branches and nodes. The load can be modelled by static and/or dynamic manner.

The special part of the power system is the active power/frequency and the reactive power/voltage controls. While the first one has a global character with central load frequency control (LFC), the second one has a local character with pilot nodes controllers. These two controllers are supervised by tertiary control.

The conceptual power sytem model is shown in the Fig.  2.

Fig.  2 Conceptual Model of the Power System

The part of the power system controlled by a common LFC is called an area and the interchange power balance is defined. The part of power system controlled by pilot node controller is called a zone.

I do not deal with the secondary reactive power/voltage controls and the tertiary control. The first one is modelled by independent module, which was created in Power Research Institute of Prague and the second one exceeds the scope of this description, because it has an economic meaning.

The unit consists of a synchronous generator, exciter and prime mover systems. Reference values Ns and Qs are the control variables. Frequency and node voltage U  are input variables.

The on load tape changers (OLTC) can be modelled by a standard model implemented in the MODES or by an automaton.

The conceptual model  of  the power system is transferred to object oriented terms of analysis and design in the following figure:

Unit

Synchronousmachine

‘UNIT’

‘EXCT’

Generator

Excitor

Constant admittance

‘LOAD’

Node

Load

Constant current

Static model

Dynamic model

Asynchronous machine

‘UNIT’

Turbine

Prime Mover

Control

‘VALV’

Boiler /PWR

DC Line

Branch

Control

Line

Switch

‘TRAN’

Generator self consumption

Static VAR Compensator

Automaton

Scenario

User

E“,d,sG ,PG ,QG ,IG ,UG

U B

R B

N T ,M T

R T

p T

Subclass

Elements

Methods

Attributes

Class

Excitation Control

‘TURB’,

‘STRC’,

‘PUMP’

Load Frequency Control

Motor

Driven mechanism

U, f ,PLOAD ,QLOAD ,ILOAD

Frequency Load Shedding

Equivalent as.motor

‘BRAN’,‘FOUL’

Transformer

On Load Tape Changing

PBRANCH,QBRANCH,IBRANCH

Tab. 1 Object Oriented Scheme of the Power System Model

The individual objects communicate between them with help messages. Sending of the message means a requirement to perform some operation - method in object oriented terms. These messages are indicated by open arrows in above scheme.

The classes encapsulate both - the data (attributes in object oriented terms) and the methods.

The Control subclasses create the supervised level from another objects. For example the frequency load shedding controls the volume of the consumption connected to some node by the method denoted as ‘LOAD’. Similary the on load tape changer controls the tape position of  some branch by the method denoted as ‘TRAN’.

The last three Control subclasses can control the all objects. The Automaton performs some action, when some predefined criteria are realised. So that it can simulate a deterministic operation of the real equipments, such a relays and protections. The Scenario Control subclass performs some subsequent actions in predefined time. So that it can simulate different accidental phenomena such faults.  The User subclass can simulate actions of dispatchers in a control center or on substation or power plant levels.

# Network Model

It is possible to neglect the electromagnetic phenomena for the purpose of electromechanical and long term transient modelling.

The network and load are considered as symmetrical, so that only the positive sequence components are taken into account. The network admittance matrix method is suitable the description. In shorthand matrix notation is simply:

Ö3*I=Y*U 										[1]

We use per unit system for dynamic calculation. The relation between per unit value (printed by italics) and named value is:

X=X/XV 										[2]

X,XV..per unit and reference values of X.

The voltage reference values are determined by nominal values in each voltage level. The reference power is an arbitrary value, which should not be very different from 'normal' power transmissions. Other rated values are then:

IV=SV/(Ö3*UV) 		ZV=UV2/SV		 YV=1/ZV			 [3]

The equation [1] has then the similar form without Ö3.

## Branch Model

The branch model represents the lines (overhead lines and cables), switches or transformers. The p scheme branch model is shown in the Fig.  3:

a) Original schema 						b) Substitute per unit schema

Fig.  3 Schema of Branch Model

The substitute scheme saves the symmetry of Y matrix. The substitute parameters are computed from input data by relations:

YSER=1/(R+jX) 		YSHUNT=jB/2.						 [4]

The per unit ratio pT is 1 for lines and switches, for transformers it is computed by:

pT=pT*UvREC/UvSEN 								[5]

where pT is no-load ratio.

### Short circuit model

The short circuit on a line is modelled by a virtual shunt DYSHUNT between the short circuit place and the zero potential place (ground). The single pole scheme for the positive sequence components is shown in the Fig. 4 :

a) Initial Schema 				b) Resulting Schema after Simplification

Fig.  4 Schema of Short Circuit Model

The additional admittance is calculated from:

DYSER=YPOM*(1-dist)*dist      DYSEN=YPOM*(1-dist)           DYREC=YPOM*dist	 [6]

DYSHUNT*YSER

YPOM=______________________

YSER +  DYSHUNT*(1-dist)*dist

dist is per unit distance between the short circuit place and the sending node.

## On Load Tape Changer Model

Some transformers serve for maintaining the voltage value between preset limits on the side, which is equipped by the on load tape changer (OLTC). This tape changing is automatically or handly controlled. The scheme of an automatically controlled OLTC, implemented in the program MODES is in the  Fig. 5:

Fig.  5 On Load Tape Changer Model

This is time dependent control, because the changing time depends on the voltage error value. The time delay is shorter for greater voltage errors and vice versa.

Another possibility to model OLTC is using of an automaton model, described later.

# Load Modelling

The possible load models are in the Fig. 6:

Fig.  6 Different Types of Load Models

The program MODES makes it possible to divide the total load in each node around the above mentioned models.

## Static Load Model

This model corresponds to so called aggregate-based representation of load modelling, when we  do not have precise information about the load composition, but we have the measuring dependent of load on the voltage and frequency.

The static model is valid for a small deviation from initial state and after the fast transients have been finished. Therefore it is suit for middle and long term dynamics. The used characteristics are:

PSTAT=P0(t)*(1-AP-BP+AP*U+BP*U2)*(1+CP*sU)					[7]

QSTAT=Q0(t)*(1-AQ-BQ+AQ*U+BQ*U2)*(1+CQ*sU)

U=abs{U}/Uv    sU=[arg{U(t+Dt)}-arg{U(t)}]/Dt/W0						[8]

where Dt is an integration step, W0 is nominal electrical speed (314 rad/s) and U is complex voltage.

The parameters of the reactive load are dependent on the power factor /2/ as:

AQ=A0/tgF  		BQ=1+B0/tgF 		CQ=C0/tgF

where A0,B0,C0 are constant parameters. The time functions P0(t) and Q0(t) may introduce step changes, ramp changes or accidental changes.

If the node voltage falls below preset value UMIN, this model changes to the constant admittance model. This situation is to be seen from on following figure, where the functin Qstat=f(u) is drawn.

Fig.  7 Static Characteristics of Load for A0=-9.5, B0=5.3  and Umin=0.8

## Induction Motor Model

There are two possibilities to model equipments driven by an asynchronous motor:

- aggregate representation  - as an equivalent  induction motor model

- component-base representation - as individual units.

The first one corresponds to the of load modelling, when we know the portion of different types of consumption, but we do not know exactly parameters of the each individual motor.

The second one corresponds to case of home consumption, when the parameters  are  know.

### Equivalent Induction Motor Model

This motor is modelled by the steady state model, when stator and rotor transients are neglected. The equivalent scheme is:

Fig.  8 Steady State Induction Motor Model

It is seen, that the rotors parameters are slip dependent, so that deep bar or double cage rotor is taken into account. The slip is calculated as:

s=(sR+sU)/(1+sU) 										[9]

The dynamics is represented by rotor slip sR :

TMsR°=MMECH-PEL/(1+sU)									[10]

The mechanical torque is:

MMECH=kZAT*cosfin*{1-A-B+A*(1-sR)/(1-sR0)+B*[(1-sR)/(1-sR0)]2}				[11]

kZAT....initial power divided by the motor nominal active power

cosfin...nominal power factor

A,B.......load characteristic parameters

sR0 ......initial rotor slip

TM .......mechanical time constant

MMECH ..mechanical torque

PEL ........electrical power		.

### Unit Model of Induction Motor

The second possibility is a ten pieces wise linearised function of slip. The special function with a swing check valve and torsion torque is available, too.

This model takes into account the electromagnetic transients. The asynchronous motor is modelled as source of an equivalent electromotive force behind of some equivalent impedance (which may consist of an external part - for example a feeding cable if it is not part of network). The one pole scheme is in the Fig. 9 :

Fig.  9 Electromagnetic Asynchronous Motor Model

The complex electromotive force is calculated for a single cage model denoted ‘ELM1’:

U' = E' + [ (R1+Rv)+j(XS-X')]I S								[12]

T0'*E '° = -sR T0'E' - { E' -j(XS-X')IS							[13]

T0'=(X' 2+Xm)/R' 2 	X'=X1 +X' 2Xm/( X' 2+Xm)	XS=X1+Xm

U' , E' ,  I S......terminal voltage, transient electromotive force and stator current

T0' ,X'..............no load transient time constant and transient reactance

XS, Xm ............stator land magnetizing reactance

R1, X'1.............stator resistance and leakage reactance

R’2, X '2...........rotor resistance and leakage reactance apparent from the stator side.

This form of equation is published in /1/ for single cage motor.  The parameters X' 2  and  R' 2  may be slip dependent (similar as in the equivalent model see Fig.8), so that it is suitable for the deep bar or double cage rotor motor modelling.

A two cages model denoted ‘ELM2’ has equations:

U' = E“+ [ (R1+Rv)+j(XS-X“)]I S								[14]

T0“*Y'° = -sR T0“ Y' - {Y'-j(XS-X')IS							[15]

E“= E' + Y'										[16]

T0“=(X' 3+ X' 2Xm/( X' 2+Xm))/R' 3	X“=X1 +X' 2 X' 3Xm/( X' 3X' 2+X' 2Xm+X' 3 Xm)

Y' ,E“..........leakage flux of the additional rotor winding and subtransient electromotive force (emf)

T0“, X“........no load subtransient time constant and subtransient reactance

R’3, X '3.....additional rotor winding resistance and leakage reactance apparent from the stator side

The parameters are constant (slip independent) in this model. The equation of motion is:

TMsR°=cosj‘n kLkC f(sR) - Re{E *I* S}							[17]

sR is the rotor slip and E is either transient (for ‘ELM1’ model) or subtransient emf (for ‘ELM2’ model).

TM= J*W02/Sn          cosj‘n =cosjn hW0/Wn    k L= M0/Mn    kC=1/f(sR0)

Sn ,Wn ,Mn......rated power, nominal angular velocity and motor torque

M0 , sR0..........mechanical torque and slip for the initial contidion.

k L...................loading factor.

f(sR) defines the shape of the torque/slip characteristic. There are implemented four types of these characteristics. The first is constant characteristic denoted as  ‘CONS’ and the others are described in the following sections.

#### Standard model

This model denoted as ‘STAN’ is described by single equation:

f(sR)= 1 - A - B + A(1- sR) + B(1- sR)2							[18]

#### Model with swing-check valve

The characteristic denoted as ‘TCHK’  Is shown in the Fig. 10:

Fig.  10 Characteristic of drive with swing-check valve, friction and hysteresis.

#### Piece wise linear model

The characteristic denoted as ‘TCHK’  Is shown in the Fig.  11:

Fig.  11 Piece wise linear charakteristic

The function f(sR) is  defined for eleven points and a linear interpolation is provided among them.

## Self Consumption Model

This model is similar as the static load model, but there is the dependency on power plant output and linear dependency on voltage only:

PAUX=P0*(1-AP-BP+AP*U+BP*PGEN/P0+CP*(1+sU)) 				[19]

QAUX=Q0*(1-AQ-BQ+AQ*U+BQ*PGEN/P0+CQ*(1+sU))

There is not possible to change P0/Q0 and to the admittance model.

## Load Frequency Shedding

The four stage load frequency shedding model is implemented in the MODES library. The each stage operates independently and its action is in the Fig.  12:

Fig.  12 Operation of Load Frequency Shedding Model

In  case 1. this stage does not operate, because the frequency recovers. In case 2, this stage after some delay,  causes the tripping of a predefined part of load.

## Constant Admittance Load Model

This admittance YLOAD is added to the diagonal element of admittance matrix. Because of these parameters are frequency independent, the influence of frequency deviation is neglected for that load.

# Unit Model

The unit consists of the synchronous generator, exciter, prime mover and theirs control systems. The coupling between the objects is in Fig.  13.

Fig.  13 Structure of Unit Model

The marked values in this figure represent the coupling variables, which create the inputs and outputs of individual objects.  The NS and   QS/US control variables have a special meaning.

The NS control variable  is reference output from LFC  and QS is a reference reactive power if the unit is controlled by pilot node controller.  US value is a reference voltage. It is created by Q controller, if the excitation operates in the reactive power control mode (secondary control).   US value is a constant value (or controlled manually), if  the excitation control operates in the  voltage control mode (primary control).

The  additional signals UEXC (output from the underexcitation limiter), LIMT (output from the stator and rotor  current limiter) and STAB (output from the power system stabiliser) are mentioned later.

## Generator Model

Because the program MODES deals with the electromechanical transient, it is possible to neglect the electromagnetic phenomena in the stator windings and to substitute the generator by its electromotive force E".  We will suppose  X"d=X"q and neglect stator resistance for simplification.  If the generator is modelled together with its step-up transformer (it is not a part of network model), the short circuit reactance and ratio are taken into account. A scheme is given below.

Fig.  14 Scheme of Unitl Model Connecting to Nodek

XT is the equivalent transformer reactance seen from generator side and pT is per unit ratio:

XT=ukSGENnSTnUTnUGENn2pT=pTUVUGENn                					[20]

uK is per unit short circuit reactance and pT is the turns number of generator side winding divided by turns number of network side winding.

### Synchronous Machine Equations

The following presumptions are taken into account:

a)	the speed deviations are small

b)	the reactance are constant parameters (no saturation)

c)	the 1st harmonic of electromotive force is taken into account

d)	the concentric excitation winding

e)	the damping winding (or massive rotor influence) is substituted by one equivalent concentric winding    in each axis

f)	the hysteresis loss and stator resistance are neglected, the  eddy current losses are covered by equivalent damping winding

It is possible to write the Park equation in per unit for the rotor windings:

Td0'*Eq'° = UE + (Xd-Xd')*Id - Eq' 							[21]

Td0"*Eq"° = Eq' + (Xd'-Xd")*Id- Eq" 							[22]

Tq0"*Ed"° = (Xq-Xd")*Iq- Ed"								[23]

Eq',Eq",Ed".....  ...d,q components of the electromotive forces

Id,Iq.....................d,q components of stator current

UE..................... ..excitation voltage

Td0',Td0",Tq0"... time constant

Xd,Xd',Xd".......... synchronous, transient and subtransient. reactance

These equations were published in /1/. The reference values are the nominal stator current, terminal voltage and no-load excitation voltage.

In this per unit system is steady state values of excitation voltage and field current the same:

Eq=IE=Eq'-(Xd-Xd')*Id 								[24]

The swing equation is:

NT           PG

TM*sG° = ________ - ______ - MAS 							[25]

1+sG         1+su

d° = sG 										[26]

sG,d ..rotor slip and absolute rotor angle -between q rotor axis  and synchronously rotating reference axis

NT......mechanical turbine power

PG......active generator power

MAS...asynchronous damping moment

TM......mechanical time constant

°..........symbol of the synchronous time derivation, where the synchronous time is:

t = t*W0											 [27]

t,W0....current time ,synchronous speed 314 rad/s.

MAS is calculated as /2/:

MAS=U221−Xd'XdsTd0'Xd1+sTd0'2+1−Xd''Xd'sTd0''Xd'1+sTd0''2+1−Xd''XqsTd0''Xq1+sTd0''2	[28]

U is terminal voltage magnitude and slip is determined as:

s = sG-sU.										[29]

The complete set of equations [21] - [26] introduces so called Park's generator model and we sign it by symbol 'PARK'.   MAS is zero in this model, because the damping is covered by rotor equations. This model is suit for transient stability calculations and in case the excitation action is to be  taken into account.

If the rotor electromagnetic transients are neglected, the Eq",Ed" electromotive force components  are constant and so called "classical" model rises. In this case it is necessary to solve the equations [25] [26] and [28]. This model is denoted 'CLAS' and it is suitable short term dynamic calculations and for modelling of generators, which are in long distance from the disturbance place, so that the voltage deviation are small.

If the rotor slip sG and angle d are constant values, we get the model denoted 'CONS'. This model makes possible to simulate the infinity bus . It is suitable for the modelling of large system influence.

The mean (system) frequency deviation is zero in that modelled power systems. The active power deficit is fully covered by infinity bus model.

If we assume that the value of system frequency fSYS is the same  in the whole power system, then the system frequency deviation is calculated as follows:

TMSYS*sSYS° = DMSYS 								[30]

TMSYS=S{TMi*SGni/SV}	 DMSYS= S{[(NTi-PGi)/(1+sSYS)-MASi]*SGni/SV} [24]

The swing equation for individual unit has form:

TM*s° = (NT-PG)/(1+sSYS)-MAS-TM* DMSYS/TMSYS    dREL° = s			 [31]

s,dREL ..electrical slip and relative rotor angle.

This model is denoted as 'EXTN' and it is suit for the long term dynamics calculations.

### Coupling between Generator and Network

The equations [21] - [24] is valid for d,q co-ordinating system, which is fixed connected with rotor. The network equation [1] is valid for synchronously rotating system. The relation between the both systems is seen from the following Fig.  15.

Fig.  15 Relation between the Co-ordinating Systems

The transformation equations are:

Eq"+jEd" = E"*exp(-jd) E" = (Eq"+jEd")*exp(jd) 						[33]

The electric variables are then calculated:

E" - pT*U      		        XT*E" + Xd"*pT*U

IG=___________ 		UG=________________	  XG=Xd"+XT 	 	[33]

jXG                         		        XG

PG=Real{UGIG*} 	QG=Imag{UGIG*} 	   UG=abs{UG}		   IG=abs{IG}

### Control Variables

The excitation voltage UE and the mechanical power NT are the input variables. These variables play an important role, because of they make possible the unit control.

The exciter and turbine are sources for these variables. They are the actuators only, and they have the own control systems. The excitation and prime mover controllers are used for unit control. We will strictly differentiate between the actuators and control systems, because of they are physically and logically independent objects. The IEEE methodology will be used for the actuators description. The common controllers were created on the base of analysis of real system operated in CENTREL power systems.

It would be noticed, that the control systems described later in this guide and implemented in the MODES program are mathematical abstractions of the real equipments. It is not guaranteed, that these models take into account all the features of the real excitation and prime mover control systems. It means, that the models structure could not correspond exactly with structure of real equipments,  but it should estimate the dynamic response of these equipments to the network disturbances.

## Excitation Modelling

The excitation of synchronous machine consists of two relatively independent part - the exciter and controller.

### Excitation Control

The base function of the excitation control is to maintain the set value of terminal voltage - it is primary control. Usually the primary controller has so called reactive current compensation, which determinates the drop of static characteristic UGEN=f(QGEN).

The excitation control may have another functions:

a)	stator and rotor current limiter, which protects the generator from the overloading of the stator and rotor circuit

b)	underexitation limiter, which does not allow the overheating  of stator winding parts, the loss of static stability and the  voltage decreasing of auxiliary consumption.

c)	power system stabilizer (PSS) serves for transients damping

d)	secondary reactive power controller, which controls the  reactive power, in this case the primary control is supervised by this secondary control.

The general-purpose excitation control model was created on the base of analysis of real controllers. This model makes possible all above mentioned functions and its scheme is in the Fig.  16:

Fig.  16 Scheme of General-purpose Excitation Control Model

The derivative feedback serves for the stabilisation of ‘AC_1’ and ‘DC_1’ exciters models. The PSS is used for ‘AC_4’ and ‘ST_1’.

The controller has PI character, the proportional mode only is possible by choosing Ti=0.

The coupling variables  are:

UE UB ...........Voltage of the exciter (for ‘DC_1’ excitation model) and the auxiliary generator voltage    		            (for ’AC_1’  excitation model - see 5.2.2)

R E ................  Output from the excitation controller

STAB.............  Power system stabiliser signal

UEXC............. Output from the underexcitation limiter

LIMT ............... Output from the stator and rotor current limiter

UG QG	...........Terminal voltage and reactive power

#### Stator and Rotor Current Limiter

The scheme of this equipment is in the Fig.  17:

Fig.  17 Scheme of Stator and Rotor Current Limiter Model

The limiter compares the actual values of stator and rotor (field) currents with their reference values. If any deviation is greater the zero the integration process starts. When the integrated value is greater then some preset value, the additional signal is subtracted from the voltage error, and the excitation voltage decreases. There are some delays between the deviation appearing and the limiter action, because some time limited overloading is allowed.

#### Underexcitation Limiter

The underexcitation limiter plays the similar role as the stator and rotor current limiter. The difference is, that it operates immediately, if the operating point fit to the not allowed area. The model is in the Fig.  18 .

Fig.  18 Scheme of Underexcitation Limiter Model

#### Power System Stabilizer

The power system stabilizers are used for fast thyristor excitation systems and serve for the electromechanical oscillation damping. The scheme is in the Fig.  19.

Fig.  19 Scheme of Power System Stabilizer Model

The power system stabilizer model works with two signals - active generator power and rotor slip (speed deviation). The each signal has the own gain. The gained signals are added and feed    the lead lag term. The output signal is symmetrically limited.

#### Secondary Reactive Power Controller

The secondary Q controller is a supervisor for primary voltage control. The scheme is in the Fig.  20:

Fig.  20 Scheme of Secondary Reactive Power Controller Model

It is possible to block the integration part of the PI controller  by TIQ=0 option. The nonlinearity term has the following functions:

a)	blocking the controller for small deviations (dead band  deQ)

b)	constraining the controller for large deviations (eQcon) caused  by a near short circuit

c)	preventing the fast changes for middle deviations (eQlim)

### Exciters

The RE output of excitation controller  controls an exciter. There are four main types of exciters used for  large units, models of which are implemented in the MODES program. Their schemes are in the Fig.  21:

Fig.  21 Structure of the Main Types of Exciters

The IEEE methodology is used (see /4/), but there is one difference. The exciters were separated from theirs controllers. The models of the exciters are shown below:

Fig.  22 Scheme of Exciter Models

The parameters for the each model are described in the following paragraphs.

#### DC Machine

The first  'DC 1'  model is usually used for smaller power up to 110MW. Field winding is feeded directly by the controller. So that gate kE and time constant TE are calculated:

RF*UE0                                                    LF

kE= ____________   [pu,A/V,V,W,V]   TE= ________  [s,H,W,pu]	 		[34]

KLIN*UREGv                                          RF* kE

LF,RF.... induction and resistance of exciter field winding

UREGv...reference value of controller voltage

UE0........no-load excitation voltage

KLIN.......line scope of loaded machine characteristic

sE ..........saturation function- see Fig.  23.

Fig.  23 DC Exciter Characteristic

The saturation is estimated by an exponential function:

RF*UE0  		    UE

sE=fS* __________ = A*exp(B ______) 						[35]

UREGv                          UEn

A,B are the parameters.

The more complex DC exciter equipment (with more field windings) should be substitute by one equivalent circuit for the casual computations.

#### AC Exciter

The second model  'AC 1' is usually used for machines up to 220MW. The excitation controller control the tyristoric bridge, which is modelled without any delay. Its gain is included in the controller gain. The transfer of auxiliary generator is modelled in a simplified manner. The models parameters is possible to compute from machine parameters /5/:

p*cosd                         3*Xd"                      2

kE=________          kC=Ö3________    kD=Ö3___(1-sdD)*Xd*pI*sind    TE=(TD+TF)/kE       [36]

Ö3*3*pU                         p*RF                       p

kE,TE..... equivalent excitation gain and time constant

Parameters of auxiliary generators are:

Xd",Xd[W].....subtransient and synchronous reactance

RF [W] .......field winding resistance

TD ,TF [s]....Time constant of damping and field windings.

The initial rotor angle d and voltage and current ratio are:

2(3/p)2*(1-sdD)*Xd/RF                Ö2*UEn                  IE0

d=argtg(___________________)    pU = _______	pI= _____			[37]

1+(3/p)*Xd"/RF 		   Ö3*UE0               Ö3*IEn

UE0,IE0.......no-load excitation voltage and current of main   generator

UEn,IEn.......nominal voltage and current of auxiliary generator

The commutation function FEX takes into account the voltage drop on non-controlled bridge /4/:

1-0.5x				 	   x<0.433

FEX= Ö(0.75-x2)   			for 0.433<x£0.75 	  x=kC*IE/UA		[38]

1.732(1-x) 		 	      0.75 <x£1.0

#### Tyristoric Exciter

This is up-to date excitation system. The voltage drop is compensate by the controller actions.

### Simplified Excitation Model

The simplified models are used in the case, when the all parameters of above mentioned models are not known or it is not necessary to use so precise models. These models are in the Fig.  24.

Fig.  24 Simplified Excitation Models

It is possible to use the model 'CONS' for not controlled exciter. The model 'STAN' can be  used for the small voltage disturbed unit, which are  located in a long distance from disturbed location.

## Prime Mover Modelling

The prime mover of the synchronous machine usually consists of the three relatively independent parts: turbine, source of operating medium and theirs control systems. The diesel engine prime mover is not implemented, so that it will not be described. The description will be as brief as possible, the reader can find more precise information in /11/.

### Turbine Controller

The origin function of the turbine controller was to maintain the speed. This function was covered by a mechanical, later hydraulic speed governor. It was the primary control.

This function is suppressed now, because the different control mode is used for parallel operation in a large power system. It is usually either the power control (classical control) or pressure control (turbine follow mode). The hydraulic speed governor may be either in operation (serial operation with supervised above mentioned electronic control) or in the reserve operation (parallel operation with supervised controllers). So that speed governor action is either temporary (serial operation with supervised PI controller), or quite eliminated (parallel operation or without speed governor). So that it is necessary to cover primary control by another equipment. The frequency corrector is used and it determinates of the drop of static characteristic NT=function (f).

The next description deals by the steam and hydro turbine control.

#### Steam Turbine Control

The up-to date steam turbine controllers may cover the next base function:

a)	speed control - is usually used for start-up, in some disturbed states or in island operation

b)	power control - the turbine power is determined by steam flow rate (by control valves) and source (boiler/reactor for  classical/nuclear  unit ) maintain the preset pressure -it is  boiler  follow mode.

c)	pressure control - the turbine power is determined by steam generation (by fuel supply for classical unit or by external reactivity -control rods for nuclear unit), pressure is maintain by control valves in preset (either constant, either variable value) - it is so called turbine  follow mode.

The basic normal control mode (power and pressure control) is shown in the Fig.  25.

Fig.  25 Fundamental Scheme of Steam Turbine Control Modes

The additional function are:

d)	acceleration relay changes the control structure

e)	fast valve closing - may be permanent (when the unit is  tripped from the system) or temporary (fast valving)

These two function have the protection meaning, because of they save from large speed deviations.

##### Prime Mover Control Model for Normal Operation

The scheme of general-purpose model of prime mover control for steam classical unit is in the Fig.  26:

Fig.  26 Scheme of General-purpose Prime Mover Control Model

This model suits for long term dynamics calculations, when the pressure deviations take place and the boiler operation is necessary to take into account.

The model is common for the both basic control modes. The choice of the control mode depends on parameter A1 value (A1=1 for the classical control - boiler follow, A1=0 for the pressure control - turbine follow). It is possible to simulate the manually control and natural sliding pressure by switching the turbine controller OFF.

Note,  there are two links between  the turbine and boiler controllers. The first one is a load anticipation (for a faster boiler response on load reference changes). The second link is a  pressure correction (for lesser pressure deviation).

##### Turbine Control Model for Special Operation

This model covers the additional functions - speed control and  acceleration relay action:

Fig.  27 Scheme of Turbine Control for Special Operation

Turbine control is switched to the Overrun Mode by an acceleration relay action.  The speed control is an optional mode. It is possible to switch turbine control to this mode from the basic control modes mentioned in the preceding chapter. This speed control may have either proportional character only (Ti2=0) or PI character.

#### Hydro Turbine Control

The up-to date electronic hydro turbine controller may cover the next functions:

a)	speed control - for not secondary controlled units or for the frequency deviations outside preset limits

b)	power control - basic operation for secondary controlled units

c)	opening control - basic for pumping operation.

The hydro turbine control models for these  functions are in the Fig.  28.

Fig.  28 Scheme of Hydro Unit Control Models

Note, that the controller has only integral part in the power control mode. The speed control is an optional mode. Turbine control is switched automatically to this mode when the frequency deviation is greater/smaller than preset values df1/df2. This controller has PIDP character, so that it can operate in parallel regime. There are two possibilities for the reference speed. Either it is set to the nominal value (1 in per unit) or it follows the opening, so that switching over from power control to the speed one is without shock.

#### Steam Turbine Control for Nuclear Unit

This controller has slightly different structure compared with one for the classical unit. This structure is seen from the following Fig.  29.

Fig.  29 Scheme of a Nuclear Unit Control Model

Both the power and pressure control are possible, but there are any links between the turbine and reactor controllers, so that they operate independently. The dead band for pressure correction has different value for positive and negative pressure deviations. The frequency correction is added to the reference power before the load rate limiter, so that the step changes should take place in this limiter.

#### Gas Turbine Control

The following figure shows the gas turbine governor model:

Fig.  30 Scheme of Gas Unit Control Model

The overrun and speed control modes are the same like for the steam turbine –see chapter 5.3.1.1.2.

### Turbine Modelling

The  output RT of turbine control models presented in previous chapters controls the medium flow rate through the turbine.  The dynamic dependence of turbine output NT on governor output RT will presented in this chapter. We will concentrate on the three main types of turbines - the steam, hydro and gas turbines.

#### Steam Turbine Model

The IEEE methodology was used for the models creation. Two types of turbine models were implemented.

'ST S' is a simplified model without the intercept valves, so that it is usable for relatively small and slow power and speed changes.

It is necessary use the more precise  'ST A' model for the fast phenomena like acceleration relay or fast valving actions. The valves nonlinearities are neglected and control/intercept valves are modelled like equivalent one. The stop valves are modelled by changing of closing speed.

Fig.  31 Scheme of Steam Turbine Models

These models take into account the variable throttle pressure, so that they are suit for long term simulations.

The fast valving can be activated by an acceleration relay or by an automaton.

#### Hydro Turbine Model

The IEEE methodology /7/ was used. The no-load flow rate and dependence on speed deviation were neglected. This model is possible to use for the Francis and Kaplan turbines close the initial operating point. It does take into account the static head deviation. It is valid, if this deviation is relatively small.

The model signed 'HYDR' is in the Fig.  32 .

Fig.  32 Scheme of Hydro Turbine Model

#### Gas Turbine Model

Dynamic model was created on the base of simplified model one shaft gas turbine published in /12/ with additional dependency on turbine speed

The model signed 'GAST' is in the following figure.

Fig.  33 Scheme of Gas Turbine Model

The turbine is modelled by static characteristic NT=function (Fuel supply). Value M0 corresponds to the power required by compressor and friction losses. Parameter kM takes into account dependency of turbine output on turbine speed and windage losses.

### Working Medium Sources

Due to the fact that we used presumption of the constant static head, there is not necessary to create a model for the hydro turbine storage. The combustor delay is possible to neglect for gas turbines.

The steam turbines remain. There is necessary distinguish between classical and nuclear units. Two models were implemented: the boiler and PWR reactor.

The IEEE methodology /6,8/ was used for the boiler model creation. This model is valid for the drum and once-through types close the initial operating point.

The simplified model was used for the core neutronics and heat transfer /9/.This model is valid for small power/pressure deviations (the control rods is not in action). The scheme from /10/ was used for the steam generator model. The scheme for the both models is in the following figure:

Fig.  34 Scheme of Boiler and PWR Models

### Simplified Prime Mover Models

There is not necessary to take into account all control functions or the pressure deviations in some cases. The simplified prime mover models are implemented for this purpose.

Fig.  35 Scheme of Simplified Prime Mover Models

The model 'CONS' is suit for not controlled units. The model 'STAN' is suit for short term dynamics calculations, when the pressure is constant and for the gas turbine. Below is the overview of the turbine control modes:

Fig.  36 Overview of  the Control Modes

# Control System and Automatics

The central load frequency control and the general automaton models will be described.

## Load Frequency Control

The analysis of the different load frequency control (LFC) schemes used in the CENTREL power systems was carried out. The common model of the LFC was created by synthesis of these schemes. The resulting model of the some abstract LFC is in the following figure.

Fig.  37 The Load Frequency Control Model

The load frequency control evaluates so called ACE - area control error. It is possible to divide this control error into two parts. Each part is processed by a separate controller.

The first one is the individual unit control. The output from PI controller is divided by the participation coefficient into the individually controlled units. If the control range is exhausted for all individually controlled units (Nsi equal NRmaxi or Nrmini) the integrator is blocked.

The second part uses two control signals Y1 and Y3, which are sent to the controlled units. So that the controlled units may be divided into two parts (e.g. into "fast' and "slow" ones) and each part has its own PI controller and a load limiter. The reference set point of the controlled units is created by the sum of the basic load Ds and the multiple of the secondary control band R and control signal Y. It is possible to load more the „slow“ units (controlled by Y3) by the bypass denoted RS. So that he „fast“ units (controlled by Y1) may be released and prepared for subsequent regulation cycle.

The regulation range of the controlled units is shown in the figure below.

Fig.  38 Regulation Ranges for Different Types of Controlled Units

The technical maximum and minimum are usually determined by nominal turbine power and limits caused by the fuel quality for steam units and the cavitations effect for hydro units. We obtain the regulation range by subtracting the primary control reserve from the technical range. This regulation range may be decrease by some technological restriction due to steam extraction for heating (when its restriction is greater then primary control reserve). The secondary control band is floating in the regulation range.

The initial operating point should be set in the middle of the secondary control band for units controlled by control signals. The initial operating point may be set elsewhere in secondary control band for units controlled individually because it is determined by a tertiary control.

## Automatics

The objects with an automatics characteristic are dispersed over the whole power system. Their individual description exceeds the scope of this guide. The general-purpose automatics model was created. It was called as automaton in preceding description and is shown in the following figure:

Fig.  39 The Scheme of  a General -purpose Automatics Model Operation

It is possible to use the following variables and parameter like inputs:

a)	the unit coupling variables, which are shown in Fig.  13 and the following another ones:

·	Akcc .. acceleration torque

·	Delt .. absolute rotor angle

·	Thet .. phase shift between the rotor axis and the terminal voltage

·	Stuf .. filtering terminal voltage slip

b)	state and algebraic variables of unit; these variables are denoted by positive and negative numbers in the model schemes

c)	magnitude, phase  and frequency deviation of a node voltage

d)	power flow and current of  a branch

e)	components of an apparent impedance, the magnitude of the voltage differences between sending and receiving ends of  a branch

f)	active and reactive consumption in a node

g)	active and reactive generation in a node

h)	active and reactive  power flows through a profile

i)	transformer ratio of a  branch

It is possible to check these inputs by two ways. The first one is a limit exceeding  and the second one is a  boundary allowed area exceeding.

The possible actions are as follows:

a)	block/unblock  of another automatics

b)	switch on/off of a branch

c)	ratio change of a branch (transformer)

d)	change of a turbine controller  structure (see chap. 2.3.3.4.)

e)	US/QS reference value  change  of a turbine controller

f)	NS /WSet reference value change of a excitation controller

g)	load change in a node

h)	trip/connect a unit

i)	pumped operation of  a hydro unit

j)	fast valving activation of a steam turbine

k)	block/unblock of a controlled  unit from LFC

These actions correspond to the real ones in a power system. The next two actions are possible in the model only:

l)	change of a sampling interval

m)	snapshot of the power system state and return to this state

The last possibility of power system control is an operator action. The user of the MODES program can simulate some "on-line" actions during the program operation. It is possible to carry out the above mentioned b) -  j) actions.

# Conclusion

I believe that this short overview of power system modelling will bring the reader a new insight into power system analysis. I would appreciate any comments or suggestions, which will help me to improve this guide..

Karel Máslo

# Reference

/1/ J.Arrillaga : Computer Modelling of Electrical Power System;

John Willey & Sons ; 1983

/2/ J.E.Gurevic : Rascoty ustojcivosti a protiavarijnoj automatiky v energosistemach;

Energoatomizdat; 1990

/3/ O.Hora : Regulacní a budící systémy synchroních stroju;

SNTL Praha; 1985

/4/ IEEE Committee Report: Excitation System Models for Power  System Stability Studies;

IEEE PAS No 2; 1981

/5/ K.Máslo: Model soustavy synchroní generátor - mustkový usmerovac;

EGÚ Praha; 1988

/6/ IEEE Working Group Report: Dynamic Models for Fossil Fueled  Steam Units in Power

System Studies; IEEE PAS No2; 1991

/7/ IEEE Working Group Report: Hydraulic Turbine and Turbine   Control Models for System

Dynamic Studies; IEEE PAS No1;1992

/8/ F.P.Mello: Boiler Models for System Dynamic Performance Studies;

IEEE PAS No1 ; 1991

/9/ J.Dolezal : Elektrárny II; CVUT Praha; 1989

/10/ V.Kola : Power Plant Models for Operator Training  Simulator;

IEEE Pas No2.; 1989

/11/ K.Máslo : Systematizace a kvantifikace regulacních  potreb ES CSFR pro regulaci P a f;

Report EGÚ Praha; 1991

/12/ A.Borghetti at all.,: Black-start simulation of a repowered thermoelectric unit representation on the IFAC conference, Brussels 2000

Table of contents

Document Conventions	1

1. Introduction

2. Power system modelling

3. Network Model

3.1 Branch Model

3.1.1 Short circuit model

3.2 On Load Tape Changer Model

4. Load Modelling

4.1 Static Load Model

4.2 Induction Motor Model

4.2.1 Equivalent  Induction Motor Model

4.2.2 Unit  Model of Induction Motor

4.2.2.1 Standard model

4.2.2.2 Model with swing-check valve

4.2.2.3 Piece wise linear model

4.3 Self Consumption Model

4.4 Load Frequency Shedding

4.5 Constant Admittance Load Model

5. Unit Model

5.1 Generator Model

5.1.1 Synchronous Machine Equations

5.1.2 Coupling between Generator and Network

5.1.3 Control Variables

5.2 Excitation Modelling

5.2.1 Excitation Control

5.2.1.1 Stator and Rotor Current Limiter

5.2.1.2 Underexcitation Limiter

5.2.1.3 Power System Stabilizer

5.2.1.4 Secondary Reactive Power Controller

5.2.2 Exciters

5.2.2.1 DC Machine

5.2.2.2 AC Exciter

5.2.2.3 Tyristoric Exciter

5.2.3 Simplified Excitation Model

5.3 Prime Mover Modelling

5.3.1 Turbine Controller

5.3.1.1 Steam Turbine Control

5.3.1.1.1 Prime Mover Control Model for Normal Operation

5.3.1.1.2 Turbine Control Model for Special Operation

5.3.1.2 Hydro Turbine Control

5.3.1.3 Steam Turbine Control for Nuclear Unit

5.3.2 Turbine Modelling

5.3.2.1 Steam Turbine Model

5.3.2.2 Hydro Turbine Model

5.3.3 Working Medium Sources

5.3.4 Simplified Prime Mover Models

6. Control System and Automatics

6.1 Load Frequency Control

6.2 Automatics

7. Conclusion

8. Reference